## Design matrix - 1
Design Fire Matrix |  | Effect
| The content is an example only and may not suit the system, application or use of a building - adaptation will be required | FENZ notification | Fire contractor notification | Building wide alarm | Building HVAC fans/dampers | Doors / gates
Cause | Manual call point (MCP) operation | Fire | Fire | Fire | off | release
| Smoke/Heat detector operation | Fire | Fire | Fire | off | release
| Fire alarm defect | Defect | Defect | - | - | -
| Fire alarm isolate | Isolate | Isolate | - | - | -
| Power failure | - | - | - | - | release

## Construct matrix - 1
Construction Fire Matrix |  | Effect
| The content is an example only and may not suit the system, application or use of a building - adaptation will be required | FENZ notification via monitor co 'ABC' | Fire contractor notification via monitor co 'ABC' | Building wide alarm | Building HVAC fan (SF-R01) / damper (FD-01) via 1 x relay | Door (MD-01) via relay
Cause | Manual call point (MCP) operation | Fire | Fire | Fire | off | release
| Smoke/Heat detector operation | Fire | Fire | Fire | off | release
| Fire alarm defect | Defect | Defect | - | - | -
| Fire alarm isolate | Isolate | Isolate | - | - | -
| Power failure | - | - | - | - | release

## Design matrix - 2
Design Fire Matrix |  | Effect
| These are examples only and may not suit the system, application or use of a building - adaptation will be required | FENZ notification | Fire contractor notification | Building wide alarm | Local alert - fire cell of origin only | Building HVAC fans/dampers | Car park supply air | Jet fans | Corridor Electrical lighting to 100% | Doors / gates | Lift | Security monitoring company | Owner | Utilities (Gas) | Fire Door hold open devices
Cause | Sprinkler operation | Fire | Fire | Fire | - | off | on | off | on | release | recall | Fire | Fire | off | -
| Sprinkler supervised valve operation | Fire | valve op | - | - | off | on | off | on | - | recall | valve op | valve op | off | -
| Sprinkler defect | Defect | Defect | - | - | - | - | - | - | - | - | Defect | Defect | - | -
| Sprinkler isolate | Isolate | Isolate | - | - | - | - | - | - | - | - | Isolate | Isolate | - | -
| Manual call point (MCP) operation | Fire | Fire | Fire | - | off | on | off | on | release | recall | Fire | Fire | off | -
| Smoke/Heat detector operation | Fire | Fire | Fire | - | off | on | off | on | release | recall | Fire | Fire | off | -
| Apartment X smoke detector operation | - | Alert X | - | Alert X | - | - | - | - | - | - | Alert X | Alert X | - | -
| Fire Door adjacent smoke detectors | Fire | Fire | Fire | - | off | on | off | on | release | recall | Fire | Fire | off | close
| Fire alarm defect | Defect | Defect | - | - | - | - | - | - | - | - | Defect | Defect | - | -
| Fire alarm isolate | Isolate | Isolate | - | - | - | - | - | - | - | - | Isolate | Isolate | - | -
| Supply Air duct detector operation | - | - | - | - | - | off | - | - | - | - | alert | alert | - | -
| Fan control override switch on | - | - | - | - | - | on | on | - | - | - | alert | alert | - | -
| Fan control override switch off | - | - | - | - | - | off | off | - | - | - | alert | alert | - | -
| Power failure | - | - | - | - | - | - | - | - | release | - | alert | alert | off | close

## Construct matrix - 2
Construction Fire Matrix |  | Effect
| These are examples only and may not suit the system, application or use of a building - adaptation will be required | FENZ notification via monitor company 'ABC' | Fire contractor notification via monitor company 'ABC' | Building wide alarm | Local alert - fire cell of origin only | Building HVAC fan (SF-R01) / damper (FD-01) via 1 x relay | Car park supply air (SF-R02) via relay | Jet fans (JF-01, JF-02) via 2 x relay | Corridor Electrical lighting to 100% via local relay | Doors (MD-01) / gates (site entry) via relay | Lift 01 via 2 x relay4 | Security company text via monitor company 'ABC' | Owner text via high level interface to BMS | Utilities - Gas solenoid G-01 via relay. Manual reset | Fire Door 103 hold open device via relay
Cause | Sprinkler operation | Fire | Fire | Fire | - | off | on | off | on | release | recall | Fire | Fire | off | -
| Sprinkler supervised valve operation | Fire | valve op | Fire | - | off | on | off | on | - | recall | valve op | valve op | off | -
| Sprinkler defect/isolate | Defect | Defect | - | - | - | - | - | - | - | - | Defect | Defect | - | -
| Manual call point (MCP) operation | Fire | Fire | Fire | - | off | on | off | on | release | recall | Fire | Fire | off | -
| Smoke/Heat detector operation | Fire | Fire | Fire | - | off | on | off | on | release | recall | Fire | Fire | off | -
| Apartment X smoke detector operation1 | - | Alert X | - | Alert X |  |  |  |  | - | - | Alert X | Alert X |  | -
| Fire door smoke detectors (D119, D120) | Fire | Fire | Fire | - | off | on | off | on | release | recall | Fire | Fire | off | close
| Fire alarm defect/isolate | Defect | Defect | - | - | - | - | - | - | - | - | Defect | Defect | -
| Supply Air duct detector operation (D101)2 | - | - | - | - | - | off | - | - | - | - | alert | alert | - | -
| Fan control override switch 1 - Carpark supply on3 | - | - | - | - | - | on | - | - | - | - | alert | alert | - | -
| Fan control override switch 1 - Carpark supply off3 | - | - | - | - | - | off | - | - | - | - | alert | alert | - | -
| Fan control override switch 2 - Jet fans on3 | - | - | - | - | - | - | on | - | - | - | alert | alert | - | -
| Fan control override switch 2 - Jet fans off3 | - | - | - | - | - | - | off | - | - | - | alert | alert | - | -
| Power failure | - | - | - | - | - | - | - | - | release | - | alert | alert | off | close
Notes:
1 | X = apartment / device detail
2 | Duct detector alarm is non latching, it will automatically reset to allow supply air fan to restart
3 | Fan control switch overrides any automatic operation
4 | Lift recall - to level 1 unless level 1 is origin of alarm, then level 2. Requires 2 relays - fire level 1; fire remainder building
5 | Reset button required to keep the HVAC equipment in fire mode if the FAP is reset (AS 1668 requirement).

## Design matrix - 3
Design Fire Matrix |  | Effect
|  | Fire alarm | [8 empty] | Mechanical |  |  | Electrical |  |  |  | Misc
| These are examples only and may not suit the system, application or use of a building, adaptation will be required | FENZ notification | Fire contractor notification | Alarm - Building wide | Alarm - Local alert in fire cell of origin only | Alarm - Zone of origin notification | Alarm - Adjacent zone notification | Escalation timer3 | Remote Display Unit | Fire alarm LED indicators Flow and level/zone | HVAC - Building fans/dampers | HVAC -Zone of origin fans/dampers | HVAC - adjacent zone fans/dampers4 | Electrical lighting | Doors / gates5 | Security monitoring company | Integrated Passive systems (fire doors) in zone of origin | Utilities (Gas) in zone of origin | Equipment (fryers, oven) in zone of origin | Nurse call | Owner
Cause | Sprinkler operation1 | Fire | Fire | Fire | - | - | - | - | Fire | on | off | - | - | on | release | Fire | - | off | off | Fire | Fire
| Sprinkler supervised valve operation | Fire | valve op | Fire | - | - | - | - | - | on | off | - | - | on |  | valve op | - | off | off | valve op | valve op
| Sprinkler defect | Defect | Defect | - | - | - | - | - | - | on | - | - | - | - |  | Defect | - | - | - | Defect | Defect
| Sprinkler isolate | Isolate | Isolate | - | - | - | - | - | - | on | - | - | - | - |  | Isolate | - | - | - | - | Isolate
| Zone MCP operation | Fire X | Fire X | - | - | Fire X | Alert | - | Fire X | on | - | off | - | on | release | Fire X | - | off | off | Fire X | Fire X
| All out evacuation switch at SVR (White Manual call point) operation | Fire | Fire | Fire | - | - | - | - | Fire | on | off | - | - | on | release | Fire | - | off | off | Fire | Fire
| Zone heat/smoke detector operation | - | Alert X | - | - | Alert | - | Start | Alert X | on | - | off | on | on | release | Alert X | - | off | off | Alert X | Alert X
| Detectors adjacent fire door operation | - | Alert X | - | - | Alert | - | Start | Alert X | on | - | off | on | on | release | Alert X | close | off | off | Alert X | Alert X
| Escalation time reached | Fire X | Fire | - | - | Fire X | Alert | - | Fire X | on | - | off | on | on | release | Fire X | - | off | off | Fire X | Fire X
| Local Remote Display Unit reset2 | - | Reset6 | - | - | Reset6 | - | Stop | Reset6 | Reset6 | - | Reset6 | Reset6 | Reset6 | Reset6 | Reset6 | Reset6 | Reset6 | Reset6 | Reset6 | Reset6
| Fire alarm defect | Defect | Defect | - | - | - | - | - | - | on | - | - | - | - |  | Defect | - | - | - | - | Defect
| Fire alarm isolate | Isolate | Isolate | - | - | - | - | - | - | on | - | - | - | - |  | Isolate | - | - | - | - | Isolate
Notes
'Fire' means evacuation tone and message
'Alert' means alert tone and staff action message
X = zone / device detail
1 | Sprinklers may be zoned, but are not in this example
2 | Where staff need the ability to reset an alert alarm - typically care, detention and special facilities such as air traffic control
3 | Upon smoke detection, client may request a timer starts. After set run time, the alarm escalates from alert fo fire in the zone of origin and alert in the adjacent zone
4 | Assuming HVAC on helps prevent smoke entering adjacent zone
5 | In this example doors are not located in secure areas (i.e. dementia care)
6 | The alarm will only reset if the detector has reset itself

## Construct matrix - 3
Design Fire Matrix |  | Effect
|  | Fire alarm | [9 empty] | Mechanical | [5 empty] | Electrical |  |  |  |  | Misc
| These are examples only and may not suit the system, application or use of a building, adaptation will be required | FENZ notification via monitor company 'ABC' | Fire contractor notification via monitor company 'ABC' | Alarm - Building wide | Alarm - Local alert in fire cell of origin only | Alarm - Zone A | Alarm - Zone B | Alarm - Zone C | Escalation timer3 | Remote Display Unit | Fire alarm LED indicators Flow and level/zone | Building HVAC fans (SF-R01/R02/R03) / damper (FD-01/02) via 1 x relay | HVAC -Zone A fan (SF- R01) via 1 relay | HVAC -Zone A -B damper (FD-01) via 1 relay | HVAC -Zone B fan (SF- R02) via 1 relay | HVAC -Zone B-C damper (FD-01/02) via 1 relay | HVAC -Zone C fan (SF- R03) via 1 relay | Corridor Electrical lighting to 100% via local relay | Doors (MD-01) / gates (site entry) via relay | Security monitoring company text via monitor company 'ABC' | Fire Door A-B hold open device via relay | Fire Door B-C hold open device via relay | Utilities - Gas solenoid G-01 for Zone C via relay. Manual reset | Fryers, oven zone C | Nurse call via high level interface | Owner text via monitor company 'ABC'
| Sprinkler operation1 | Fire | Fire X | Fire | - | Fire | Fire | Fire | - | Fire | on | off | off | close | off | close | off | on | release | Fire | - | - | off | off | Fire X | Fire X
| Sprinkler supervised valve operation | Fire | valve op | Fire | - | Fire | Fire | Fire | - | - | on | off | off | close | off | close | off | on | - | Fire | - | - | off | off | - | valve op
| Sprinkler defect | Defect | Defect | - | - | - | - | - | - | - | on | - | - | - | - | - | - | - | - | Defect | - | - | - | - | - | Defect
| Sprinkler isolate | Isolate | Isolate | - | - | - | - | - | - | - | on | - | - | - | - | - | - | - | - | Isolate | - | - | - | - | - | Isolate
| Zone A MCP operation | Fire | Fire A | - | - | Fire | Alert | - | - | Fire AX | on | - | off | close | on | - | - | on | release | Fire | - | - | - | - | Fire AX | Fire A
| Zone B MCP operation | Fire | Fire B | - | - | Alert | Fire | Alert | - | Fire BX | on | - | on | close | off | close | on | on | release | Fire | - | - | - | - | Fire BX | Fire B
| Zone C MCP operation | Fire | Fire C | - | - | - | Alert | Fire | - | Fire CX | on | - | - | - | on | close | off | on | release | Fire | - | - | off | off | Fire CX | Fire C
| All out evacuation switch at SVR (White Manual call point) operation | Fire | Fire X | Fire | - | Fire | Fire | Fire | - | Fire | on | off | - | - | - | - | - | on | release | Fire | - | - | off | off | Fire X | Fire X
| Zone A heat/smoke detector operation | - | Alert A | - | - | Alert | - | - | Start | Alert AX | on | - | off | close | on | - | on | on | release | Alert | - | - | - | - | Alert AX | Alert AX
| Zone B heat/smoke detector operation | - | Alert B | - | - | - | Alert | - | - | Alert BX | on | - | off | close | off | close | on | on | release | Alert | - | - | - | - | Alert BX | Alert BX
| Zone C heat/smoke detector operation | - | Alert C | - | - | - | - | Alert | - | Alert CX | on | - | off | - | on | close | on | on | release | Alert | - | - | off | off | Alert CX | Alert CX
| Detectors adjacent fire door A-B operation | - | Alert X | - | - | Alert | Alert |  | - | Alert X | on | - | - | close | - | - | on | on | release | Alert | close |  | - | - | Alert X | Alert X
| Detectors adjacent fire door B-C operation | - | Alert X | - | - | - | Alert | Alert | - | Alert X | on | - | - | - | - | close | on | on | release | Alert |  | close | - | - | Alert X | Alert X
| Escalation time reached (Zone A) | Fire | Fire | - | - | Fire | Alert | - | - | Fire A | on | - | off | - | on | - | on | on | release | Fire | - | - | - | - | Fire X | Fire X
| Local Remote Display Unit reset2 | - | Reset6 | - | - | - | - | Reset6 | Stop | Reset6 | Reset6 | - | Reset6 | Reset6 | Reset6 | Reset6 | Reset6 | Reset6 | Reset6 | Reset6 | Reset6 | Reset6 | no | Reset6 | Reset6 | Reset6
| Fire alarm defect | Defect | Defect | - | - | - | - | - | - | - | on | - | - | - | - | - | - | - | - | Defect | - | - | - | - | - | Defect
| Fire alarm isolate | Isolate | Isolate | - | - | - | - | - | - | - | on | - | - | - | - | - | - | - | - | Isolate | - | - | - | - | - | Isolate
Notes
'Fire' means evacuation tone and message, 'Alert' means alert tone and staff action message
X = zone / device detail
In this example Zone A is adjacent to B, B adjacent to A&C, C adjacent to B
1 | Sprinklers may be zoned, but are not in this example
2 | Where staff need the ability to reset an alert alarm - typically care, detention and special facilities such as air traffic control
3 | Upon smoke detection, client may request a timer starts. After set run time, the alarm escalates from alert fo fire in the zone of origin and alert in the adjacent zone
6 | The alarm will only reset if the detector has reset itself
Terminology / operational naming to be confirmed by client

## Design matrix - 4
Design Fire Matrix |  | Effect
|  | Fire alarm | [5 empty] | Mechanical | [9 empty] | Electrical | [7 empty] | Misc
| These are examples only and may not suit the system, application or use of a building, adaptation will be required | FENZ notification | Fire contractor notification | Alarm - Building wide | Alarm - Zone X notification | Alarm - Zone Y notification | Fire alarm LED indicators Flow and level/zone | HVAC - Building fans/dampers | HVAC -Zone X fans/dampers | HVAC - Zone Y fans/dampers | Fire fans, make up air… | Smoke purge system | Pressurisation system - Stairwell | Pressurisation system - Lift shaft | Fans - Car park supply air | Fans - Jet fans etc | BMS | Active signage | Electrical lighting | UPS control | Emergency generator Diesel supply | Doors / gates | Security monitoring company | Communication system (PA, TV, Audio) | Integrated Passive systems (curtains, doors, dampers…) | Refrigeration system | Utilities (Gas, Water, Solar…) | Systems (burners, pumps, boilers, UPS...) | Auotmated Equipment (conveyor, crane…) | Equipment (fryers, oven, …) | Hazardous process | Lift | Fire prevention systems | Owner
Cause | Sprinkler Level/Zone X flow switch operation | Fire | Fire X | - | Fire | Alert | on | - | off | - | on | on | on | on | on | off | Fire X | on | on | off | off | release | Fire X | Fire X | - | off | off | off | stop | off | off | recall | - | Fire X
| Sprinkler Level/Zone Y flow switch operation | Fire | Fire Y | - | Alert | Fire | on | - | - | off | on | on | on | on | - | - | Fire Y | on | on | - | - | release | Fire Y | Fire Y | - | off | off | off | stop | off | off | recall | - | Fire Y
| Sprinkler Pump running | Fire | pump on | - | - | - | on | - | - | - | - | - | - | - | - | - | pump on | - | - | - | - | - | pump on | - | - | - | - | - | - | - | - | - | - | pump on
| Sprinkler supervised valve operation | Fire | valve op | - | - | - | on | - | - | - | - | - | - | - | - | - | valve op | - | - | - | - | - | valve op | - | - | - | - | - | - | - | - | - | - | valve op
| Sprinkler defect | Defect | Defect | - | - | - | on | - | - | - | - | - | - | - | - | - | Defect | - | - | - | - | - | Defect | - | - | - | - | - | - | - | - | - | - | Defect
| Sprinkler isolate | Isolate | Isolate | - | - | - | on | - | - | - | - | - | - | - | - | - | Isolate | - | - | - | - | - | Isolate | - | - | - | - | - | - | - | - | - | - | Isolate
| Level/Zone X Manual Call Point operation | Fire X | Fire X | - | Fire | Alert | on | - | off | - | on | on | on | on | on | off | Fire X | on | on | off | off | release | Fire X | Fire X | - | off | off | off | stop | off | off | recall | on | Fire X
| Level/Zone Y Manual Call Point operation | Fire Y | Fire Y | - | Alert | Fire | on | - | - | off | on | on | on | on | - | - | Fire Y | on | on | - | - | release | Fire Y | Fire Y |  | off | off | off | stop | off | off | recall | on | Fire Y
| All out evacuation switch at SVR (White Manual call point) operation | Fire | Fire | Fire | - | - |  | off | off | off | on | on | on | on | on | off | Fire | on | on | off | off | release | Fire | Fire | - | off | off | off | stop | off | off | recall | on | Fire
| Level/Zone X detector operation | Fire X | Fire X | - | Fire | Alert | on | - | off | - | on | on | on | on | on | off | Fire X | on | on | off | off | release | Fire X | Fire | - | off | off | off | stop | off | off | recall | on | Fire X
| Level/Zone Y detector operation | Fire Y | Fire Y | - | Alert | Fire | on | - | - | off | on | on | - | - | - | - | Fire Y | on | on | - | - | release | Fire Y | Fire | - | off | off | off | stop | off | off | recall | on | Fire Y
| Detectors adjacent Zone Y fire door operation | Fire Y | Fire Y | - | Alert | Fire | on | - | - | off | on | on | - | - | - | - | Fire Y | on | on | - | - | release | Fire Y | Fire | close | off | off | off | stop | off | off | recall | on | Fire Y
| Fire alarm defect | Defect | Defect | - | - | - | on | - | - | - | - | - | - | - | - | - | Defect | - | - | - | - | - | Defect | - |  | - | - | - | - | - | - | - | - | Defect
| Fire alarm isolate | Isolate | Isolate | - | - | - | on | - | - | - | - | - | - | - | - | - | Isolate | - | - | - | - | - | Isolate | - | - | - | - | - | - | - | - | - | - | Isolate
| Gas suppression detection stage 1 | - | Alert | - | - | - | on | - | - | - | - | - | - | - | - | - | Alert | on | - | - | - | - | Alert | - | - | - | - | - | - | - | - | - | - | Alert
| Gas suppression detection stage 2 | Fire | Fire | - | Alert | - | on | - | off | - | - | - | - | - | - | - | Fire | on | - | - | - | - | Fire | - | - | - | - | - | - | - | - | - | - | Fire
| Gas suppression discharge pressure switch | Fire | Fire | - | Alert | - | on | - | off | - | - | - | - | - | - | - | Fire | on | - | - | - | - | Fire | - | - | - | - | - | - | - | - | - | - | Fire
| Gas suppression defect | Defect | Defect | - | - | - | on | - | - | - | - | - | - | - | - | - | Defect | on | - | - | - | - | Defect | - |  | - | - | - | - | - | - | - | - | Defect
| Gas suppression isolate | Isolate | Isolate | - | - | - | on | - | - | - | - | - | - | - | - | - | Isolate | on | - | - | - | - | Isolate | - |  | - | - | - | - | - | - | - | - | Isolate
| Air handling duct detector operation | - | - | - | - | - | - | - | - | - | off | off | off | off | off | - | Alert | - | - | - | - | - | Alert | - | close | - | - | - | - | - | - | - | on | Alert
| Fan control switch on | - | - | - | - | - | - | - | - | - | on | on | on | on | on | on | Alert | - | - | - | - | - | Alert | - | - | - | - | - | - | - | - | - | on | Alert
| Fan control switch off | - | - | - | - | - | - | - | - | - | off | off | off | off | off | off | Alert | - | - | - | - |  | Alert | - | - | - | - | - | - | - | - | - | on | Alert
| Fire prevention system defect/isolate | - | Alert | - | - | - | on | - | - | - | - | - | - | - | - | - | Alert | on | - | - | - | - | Alert | Alert | - | - | - | - | - | - | - | - | Alert | Alert
| Ammonia warning | - | Warning | Warning | - | - | on | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Warning | Warning | - | - | - | - | - | - | - | - | - | Alert
| Power failure | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Alert | - | - | - | - | release | Alert | - | - | - | - | - | - | - | - | - | - | Alert
| Fireman's Service lift key switch | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | control | - | -

## fire alarm relay sched
Fire Alarm Relay (FAR) Checklist - EXAMPLE |  |  |  | <---------------------------Fire Alarm Contractor-------------------> |  |  |  | <------------Interfacing Contractor------------> |  |  | Integrated Testing
FAR Reference | Location | Trade Interface | Description | FAR Address | FAR Installed | FAR Programmed | FAR Successful Test | Installed | Terminated | Successful Test | End-To End Successful test | Comments
FAR-1 | Level 5 Plant room | Mechanical | Mechanical supply air shutdown (SF-01) damper close (FD-01) | xx-xx-xxx | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | Witness by ABC Main Contractor hh-DD-MM-YYYY
FAR-2 | Basement plant room | Mechanical | Car park supply air on (SF-R02) | xx-xx-xxx | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | Witness by XYZ Fire Engineer, hh-DD-MM-YYYY
FAR-3 | Basement plant room | Mechanical | Jet fans shutdown (JF-01 & JF-02) | xx-xx-xxx | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | Witness by XYZ Fire Engineer, hh-DD-MM-YYYY
FAR-4 | Basement switch room | Electrical | Corridor Electrical lighting to 100% | xx-xx-xxx | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | Witness by ABC Main Contractor hh-DD-MM-YYYY
FAR-5 | Ground level Equipment cupboard | Security | Access Control: Door MD01 release, site gates release | xx-xx-xxx | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | Witness by XYZ Fire Engineer, hh-DD-MM-YYYY
FAR-6 | Level 5 Lift Controller 1 | Lift | Automatic lift recall to ground level | xx-xx-xxx | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | Witness by XYZ Fire Engineer, hh-DD-MM-YYYY
FAR-7 | Level 5 Lift Controller 1 | Lift | Automatic lift recall to level 1 | xx-xx-xxx | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | Witness by XYZ Fire Engineer, hh-DD-MM-YYYY
FAR-8 | Basement plant room | Hydraulic | Gas solenoid G-01 shutdown, manual reset | xx-xx-xxx | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | Witness by ABC Main Contractor hh-DD-MM-YYYY
FAR-9 | Level 1 services cupboard | Builder | Fire door 103 hold open device release | xx-xx-xxx | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | Witness by XYZ Fire Engineer, hh-DD-MM-YYYY
HL-1 | Basement plant room | Mechanical | Owner notification through BMS | xx-xx-xxx | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | ✓ | Witness by ABC Main Contractor hh-DD-MM-YYYY
Instructions: | [6 empty] | All interfaces have been successfully tested in accordance with the Fire Matrix
1. Fire Alarm Contractor to identify all Fire Alarm Relays (FAR)required to achieve Approved Integrated Fire Cause & Affect Matrix functionality | [6 empty] | Project
2. FAR locations to be agreed with interfacing contractors e.g. adjacent a Mechanical Distribution Board, or a security controller (as close as possible) | [6 empty] | Signed
3. Fire Contractor to programme FAR according to Fire Matrix requirements and test functionality independently of interface trade. | [6 empty] | Company
4. Interface trade to install and terminate cabling between FAR and interface equipment and test independently of Fire Alarm trade | [6 empty] | Date
5. Combined or end-to-end testing to be carried out e.g. activation of a MCP to verify mechanical fan shutdown, or release of specific access controlled doors.