Commissioning Issues Register

Instructions: Commissioning defects to be recorded in the defect register to ensure they are rectified by the responsible party, checked, and re-tested.

| No. | Date Observed | Interface | Description | Reason/Corrective Action | Responsible | Date Rectified | Checked | Status | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 12/06/2019 | Lifts | Lift failed to return to ground floor on fire signal | Wiring between the fire alarm relay and lift controller was found to be incorrectly terminated at lift controller. Lift Contractor to rectify and re-test. | Lift Contractor | 13/06/2019 | ✓ | Closed |  |
| 2 | 13/06/2019 | Mechanical | AHU-2-3 continued to run when the duct smoke detector was activated. | Faulty duct smoke detector to be replaced | Mechanical Contractor |  |  | Open | Awaiting delivery of replacement detector. |
| 3 | 13/06/2019 | Security | Egress door D-110.1 remained locked on activation of the fire alarm. | Fire Alarm incorrectly programmed | Fire Contractor | 13/06/2019 | ✓ | Closed |  |