Integrated Systems Testing checklist

The content is an example only and may not suit the system, application, or use of a building - adaptation will be required.

Where buildings are zoned or equipment is to operate independently, more detailed cause and effects will need to be entered.

| Project |  |
| --- | --- |
| Address |  |
| Signed/Name |  |
| Company |  |

Notes to include which items have been tested:

| System input | System output | Action | Notes | Test results | Date | Initials |
| --- | --- | --- | --- | --- | --- | --- |
| - Sprinkler operation (FBA signals fire) | - FENZ notification | Fire |  |  |  |  |
|  | - Fire contractor notification | Fire |  |  |  |  |
|  | - Building wide alarm | Fire |  |  |  |  |
|  | - Building HVAC fans/dampers | Off |  |  |  |  |
|  | - Car park supply air | On |  |  |  |  |
|  | - Jet fans | Off |  |  |  |  |
|  | - Corridor Electrical lighting to 100% | On |  |  |  |  |
|  | - Doors / gates | Release |  |  |  |  |
|  | - Lift | Recall |  |  |  |  |
|  | - Security monitoring co | Fire |  |  |  |  |
|  | - Owner | Fire |  |  |  |  |
|  | - Utilities (Gas) | Off |  |  |  |  |
| - Sprinkler supervised valve operation | - FENZ notification | Fire |  |  |  |  |
|  | - Fire contractor notification | Fire |  |  |  |  |
|  | - Building wide alarm | Fire |  |  |  |  |
|  | - Building HVAC fans/dampers | Off |  |  |  |  |
|  | - Car park supply air | On |  |  |  |  |
|  | - Jet fans | Off |  |  |  |  |
|  | - Corridor Electrical lighting to 100% | On |  |  |  |  |
|  | - Doors / gates | Release |  |  |  |  |
|  | - Lift | Recall |  |  |  |  |
|  | - Security monitoring co | Fire |  |  |  |  |
|  | - Owner | Fire |  |  |  |  |
|  | - Utilities (Gas) | Off |  |  |  |  |
| - Sprinkler defect/isolate | - Fire contractor notification | Defect |  |  |  |  |
|  | - Security monitoring co | Defect |  |  |  |  |
|  | - Owner | Defect |  |  |  |  |

Integrated Systems Testing checklist - continued

| - Manual call point (MCP) operation | - FENZ notification | Fire |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | - Fire contractor notification | Fire |  |  |  |  |
|  | - Building wide alarm | Fire |  |  |  |  |
|  | - Building HVAC fans/dampers | Off |  |  |  |  |
|  | - Car park supply air | On |  |  |  |  |
|  | - Jet fans | Off |  |  |  |  |
|  | - Corridor Electrical lighting to 100% | On |  |  |  |  |
|  | - Doors / gates | Release |  |  |  |  |
|  | - Lift | Recall |  |  |  |  |
|  | - Security monitoring co | Fire |  |  |  |  |
|  | - Owner | Fire |  |  |  |  |
|  | - Utilities (Gas) | Off |  |  |  |  |
| - Smoke/Heat detector operation | - FENZ notification | Fire |  |  |  |  |
|  | - Fire contractor notification | Fire |  |  |  |  |
|  | - Building wide alarm | Fire |  |  |  |  |
|  | - Building HVAC fans/dampers | Off |  |  |  |  |
|  | - Car park supply air | On |  |  |  |  |
|  | - Jet fans | Off |  |  |  |  |
|  | - Corridor Electrical lighting to 100% | On |  |  |  |  |
|  | - Doors / gates | Release |  |  |  |  |
|  | - Lift | Recall |  |  |  |  |
|  | - Security monitoring co | Fire |  |  |  |  |
|  | - Owner | Fire |  |  |  |  |
|  | - Utilities (Gas) | Off |  |  |  |  |
| - Apartment smoke detector operation | - Fire contractor notification | Alert |  |  |  |  |
|  | - Local alert - fire cell of origin only | Alert |  |  |  |  |
|  | - Security monitoring co | Alert |  |  |  |  |
|  | - Owner | Alert |  |  |  |  |
| - Adjacent smoke detector | - Integrated Passive systems (Door hold open devices) | Close |  |  |  |  |
| - Air handling duct detector operation | - Car park supply air | Off |  |  |  |  |
|  | - Security monitoring co | Alert |  |  |  |  |
|  | - Owner | Alert |  |  |  |  |
| - Fan control switch on | - Car park supply air | On |  |  |  |  |
|  | - Jet fans | On |  |  |  |  |
| - Fan control switch off | - Car park supply air | Off |  |  |  |  |
|  | - Jet fans | Off |  |  |  |  |
| - Power failure | - Doors / gates | Release |  |  |  |  |
|  | - Security monitoring co | Alert |  |  |  |  |
|  | - Owner | Alert |  |  |  |  |
|  | - Utilities (Gas) | Off |  |  |  |  |
|  | - Integrated Passive systems (Door hold open devices) | Close |  |  |  |  |